[image: image1]                                                                      Baxi S.p.A.
                                                                      36061 Bassano del Grappa (VI)
                                                                       Italy
                                                                      Via Trozzetti, 20
                                                                       Tel: +39 0424 517111
code 8435400 -  NTC SENSOR
[image: image13.jpg]Z\
BAXI




Characteristics :  temperature sensor
Technical characteristics :
- Body: Brass UNI 12164 CW602N (ADZ-SBN-WRC PFS 1983:2) Dezincification resistant brass

- Finishing: raw

- Connector: 2 pin 2,5 pitch

  (Ref. 2,5 Lumberg type MSF Red color)

- Filling: high thermal conductivity epoxy resin

- Sensitive element: Thermistor (NTC)

- Nominal resistance (25°C): 10000 ohm ± 2%

- Temperature coefficient: ß (25° - 85°C) 3977 ± 1,5%

- Measuring range: - 30° to 125°C

- Response time: 5 seconds max (25°÷85°C - 63,2%)

- Insulation voltage: 1500Vac (1")

- Resistance at 30°C: 7810-8300 ohm

- Resistance at 65°C: 1930-2220 ohm

- Resistance at 85°C: 960-1175 ohm
Material : 
- Body: Brass UNI 12164 CW602N (ADZ-SBN-WRC PFS 1983:2) Dezincification resistant brass

- Finishing: raw

Weight :   0.016 Kg  (net. 0.008 Kg )
[image: image14.emf][image: image2][image: image3][image: image4][image: image5][image: image6][image: image7][image: image8][image: image9][image: image10][image: image11][image: image12]
